Section 15622									AA Series      (12/15/03)

Direct Gas Fired [Make-Up Air / Displacement Ventilation / Space Heating] System

Note: 	Optional items and/or items requiring a choice, are shown between brackets and/or parentheses with selections separated by a forward slash, i.e.[a / b / c] (a / b / c) {a / b/ c}.

# Part 1: GENERAL

1.1 Section Includes:

A. Direct Gas-Fired Heaters

B. Controls

C. Equipment Schedule

1.2 Related Sections:

A. Section 01655: Starting up mechanical systems

B. Section 15070: Pipe and pipefittings

C: Section 15100: Valves

D: Section 15120: Piping specialties

E: Section 15400: Plumbing system

F: Section 15990: Testing, adjusting and balancing

G: Section 16050: Basic electrical materials and methods

1.3 References

A. American National Standards Institute (ANSI): Establishes requirements          	     applicable to certifying direct gas-fired heaters.

B. ETL Testing Laboratories: Independent testing facility certifies standards              	   	    conformance.

C. American Conference of Governmental Hygienists (ACGIH): Establishes air 	     quality standards.

D. Environmental Protection Agency (EPA): Enforces outdoor air quality standards.

E. Occupational Safety & Health Administration (OSHA): Enforces air quality 	     standards and safety in the work place.

F. National Electric Code (NEC): Establishes electrical standards.

G. Underwriters Laboratory (UL): Independent testing facility certifies component 	     conformance to appropriate standards.

H. National Fire Protection Agency (NFPA): Establishes fire prevention standards.

I.  Factory Mutual Insurance (FM): Certifies gas manifold to owners insurance carrier.

J.  Industrial Risk Insurance (IRI): Certifies gas manifold to owners insurance carrier.

K. Sheet Metal & Air Conditioning Contractors National Association 	(SMACNA):       Sets standards for sheet metal fabrication and insulation.

1.4 Quality Assurance

Manufactures shall:

- Provide direct gas-fired heater built in conformance to NFPA-54 and certified to 	 the Z83.18 standard for recirculating type units and/or the Z83.4 standard for non-

recirculating type units, and shall be ETL Listed.

B. Provide direct gas-fired heating equipment that does not exceed contaminant 	     	     threshold limits for safe environment, as established by the ACGIH or OSHA.

C. Furnish proof, satisfactory to the owner (or its representative), of having manufactured      the specified type direct gas-fired space heating systems for a minimum of 10 years.

D. Make its facility available to owner or its representative for quality control audit 	     without prior notification.

1.5 Submittals

A. Manufacturer shall submit product data, including dimensions, duct & service 	     	     connections, accessories, controls with schematics and sequence of operation, 	     	     electrical nameplate data, wiring diagrams, fan curves and burner & filter data.

B. Manufacturer shall furnish rigging, assembly, and installation instructions.

C. Manufacturer shall furnish Operation & Maintenance Manuals, including 	     	     descriptive literature, operation instructions, maintenance and repair data, and 	     	     parts listings.

2.1 Acceptable Manufacturers

AbsolutAire, Inc. (Kalamazoo, MI)	(269) 382-1875

2.2 Direct Gas-Fired Heaters

Manufacturer shall:

- Provide a direct gas-fired [Rooftop / Horizontal / Suspended / Upright] heater with [100% O.A. {constant volume/variable volume/2-speed} / 80%/20% RA/OA {two

position/fixed/modulating}recirculation] model.

- Provide self-contained packaged heater(s) that include casing, modulating burner, non-overloading fan, fan motor and drives, mixing chamber, positive position dampers, and automatic controls (for both temperature and pressure).

- Provide a casing which shall be a minimum 18-gauge aluminized steel (16-gauge on

AA-7and AA8) welded to structural steel framing.  Both interior and exterior structural steel shall be mill primed with oxide enamel.  All exterior casing seams shall be 100% weather-tight.  All interior and exterior surfaces will be cleaned of all oil and grease.  Painted exterior will consist of a high-quality catalyzed primer coat and a finish coat of machine enamel with rust inhibitors.  Color is may selected by the owner.  [All interior surfaces will be lined with 1 inch thick, 1-1/2 pound density, coated fiberglass. The insulation shall comply to UL standard 181 for erosion and NFPA 90A for fire resistance.  All exposed edges will be coated to eliminate erosion.  Fiberglass will be held in place with both adhesive and welded pins, per SMACNA standards].  Provide a minimum of (2) hinged access doors with positive latching, watertight handles.  All access doors shall be painted on the interior and exterior and shall include braces that lock the hinged doors open during servicing.

- Filters: [Provide 1" aluminum filters accessible from the unit inlet hood to filter outdoor air / a filter mix-box to filter outdoor and return air {return air model}/ a side access v-bank filter section to filter outdoor air].  Filters shall be [polyester media in galvanized locking frames / 30% pleated disposable type / Aluminum mesh washable type / Polyester media {dust-lok / poly-link} with internal wire frame linked together to be continuous across the full width of the filter housing]. [Provide a clogged filter warning (light / alarm / photohelic) at the unit main / remote panel].

- Provide a direct-fired gas burner which shall be [Maxon Model NP1LE or NP2LE /

Midco Model HMA2 / Eclipse Model Ah-MA] specifically designed to burn natural gas or propane below the maximum non-contaminating levels required by OSHA and the ACGIH.  Burner shall have non-clogging, stainless steel baffles attached to a [cast-iron / cast aluminum] gas supply section with no moving parts.  The burner shall be capable of a 30-to-1 turndown ratio and be designed for 100% thermal efficiency for the life of the equipment.  The outdoor air velocity across the burner shall be constant and be at an air velocity necessary for ANSI certification.  The burner velocity shall be constant at all times throughout the operation of the heater.  No air from the indoor space shall be allowed to recirculate across the burner at any time. Service access to the burner igniter, UV Scanner and/or flame rod shall be accomplished through an access door or panel.

- The burner pilot system will consist of (choose one):

Direct Spark Ignition (for burner capacities up to and including 975 mbh).  Consists of an ignition module, spark igniter and flame rod to verify burner low fire ignition before allowing the gas valve to fully open.

Interrupted Piloted Ignition (for all burners).  Consists of a high voltage ignition transformer, spark igniter and UV scanner which proves pilot before allowing the gas valve to fully open.  The pilot system consists of a pilot line gas regulator, gas valve and 3/8” OD tin-lined copper tubing.

- Supply fan shall be a double-width, double-inlet, centrifugal design, belt driven for the required air capacity. The motor shall be 1750 rpm, standard NEMA frame, [Open Drip Proof (ODP) / Totally Enclosed Fan Cooled (TEFC) / EPACT compliant / Premium Efficient / Automotive Duty (7EH)] with a minimum efficiency of _____% mounted on an adjustable slide base [with a single / double] adjustment screw.  The motor shall have a 1.15 service factor, suitable for continuous service at 120° F ambient temperature, and shall be wired for the specified voltage.  Blower, motor and drive shall be factory tested to ensure the specified air delivery (per ANSI standards) at the design total static pressure.  Fan shaft shall be connected to the motor by a

V-belt drive, capacity designed for 30% over the motor nameplate horsepower.  Fan

shaft shall be a turned, ground and polished solid shaft. A protective coating shall be

applied to the shaft to minimize oxidation.  Fan shall have ball bearings, and shall be designed for a minimum L10 life of 100,000. [Fan bearings shall have extended lubrication lines, which shall terminate at the unit exterior so lubrication can be performed while the unit is in operation].

H. Provide the following Control Systems:

1. The main control panel shall NEMA 3R and contain all standard electrical components, such as [non] fused disconnect switch, motor starter, 120-volt and 24-volt control transformers, control circuit fuses, a number-coded terminal strip, and an ignition module [flame relay] to lockout the flame in abnormal conditions. The complete control and safety system as well as the burner and gas manifold shall be factory tested prior to shipment.

2. Temperature controls shall be a solid-state system located in the above main control panel.  It shall have a sensor located in the supply air stream [and/or space] as shown on the plans.  The sensor(s) control the maximum and minimum supply air temperature [and room temperature] in response to heating requirements.

3a. Automatic building pressure control [with manual override] for variable volume 100% OA models shall consist of a variable frequency drive (VFD) for supply fan speed control and a burner profile damper with a pressure differential switch to control and maintain the proper burner airflow across the burner profile.  Includes a building pressure differential switch to signal the VFD to vary fan speed as needed in response to the building negative or positive conditions.  This [diaphragm/photohelic] switch is

mounted in the heater main control panel.  The pressure sensing range shall be .01 to .20” w.c. with a null span of .02 to .03 inches water column.  [Includes a manual-automatic selector switch and a potentiometer located inside the remote control panel to allow selection of manual or automatic speed control. The potentiometer shall have an adjustment dial of with a range of 35-100% to allow adjustment of fan motor speed from 35-100%].

3b. Automatic building pressure control [with manual override] for return air model units to vary the ratio of outside air (OA) and return air (RA) from 100% OA and 0% RA to 20% OA and 80% RA.  This model shall include a separate OA/RA mixing chamber with mechanically and electronically linked OA and RA parallel blade dampers (16 gauge galvanized construction) to work opposite each other. Modulating direct-shaft coupled damper actuators controls the dampers.  Includes a building pressure differential switch to signal the OA/RA dampers to open/close to vary the amount of OA/RA needed to satisfy the building pressure switch setting.  This [diaphragm / photohelic] switch is mounted in the heater main control panel.  The pressure sensing range shall be .01 to .20” w.c. with a null span of .02 to .03 inches water column.  [Includes a manual-automatic selector switch and a potentiometer located inside the remote control panel to allow selection of manual or automatic control of the OA/RA dampers. The potentiometer shall have an adjustment dial of with a range of 20-100% to allow adjustment of OA from 20-100% and RA from 80% to 0%].

4. The remote control panel (rcp) shall be provided which incorporates the required heater operating switches and circuit analyzer lights.  The remote control panel shall be painted mild steel.  It shall include a numbered terminal strip, a summer-off-winter switch, a fan on indicator light, a burner on indicator light, a burner alarm light and a burner reset pushbutton switch.  The unit serial number and customer tag number will be on the panel face.  The cover will be key locked to prevent internal access to unauthorized personnel.  The following optional items are included which are specific to this application and specification:

- Discharge temperature dial

- Space temperature dial (the room sensor shall be field mounted per plans).

- Unoccupied space temperature dial

- Manual/auto pressure control selector switch

- Manual pressure control potentiometer

- Mechanical [electronic programmable with battery back up] 7-day time clock (Specify purpose in detail)

- Burner (off) alarm horn with silence switch

- Low temperature alarm light

5. Low temperature limit switch turns the fan motor off when cold air is being discharged from the heater.  The minimum discharge temperature may be selected from 0°F to 70°F (factory preset at ___°F). An integral timer shall by-pass this switch for 5 minutes at initial unit start-up.

6. The high-temperature limit switch turns the burner off when the discharge air temperature exceeds 120° F.  The burner must then be manually reset at the heater.

I.  Provide a gas manifold which shall be sized for the rated BTU (MBH) capacity as

scheduled on the drawings. The gas manifold will be constructed in conformance to:

- ANSI Standards

- Factory Mutual (FM) insurance requirements

- Industrial Risk Insurers (IRI) insurance requirements.

J.  Provide high and low gas-pressure switches.  The high gas-pressure switch is located       on the burner end of the gas manifold and shall turn the burner off when the gas

pressure is too high.  The maximum gas-pressure range will be from 3" to 21" w.c.     This is factory set at ____” w.c.  The low gas-pressure switch is located on the inlet end of the manifold and shall turn the burner off when the gas pressure is too low.  The minimum gas pressure range will be from 3" to 21" w.c. This switch shall be factory set at ____” w.c.

2.3 Accessories (select accessories as desired.  Manufacturer shall provide the following accessories:

A. Roof Curb

Each heater shall have a full-perimeter, 20" high curb, formed of 16-gauge aluminized or galvanized steel.  Contractor shall shim the curb so that it is level [and shall install 	 a cant strip and wood nailer per detail on the plans].

B. Service platforms

Heater shall be furnished with a service platform, running the full length (width on an upright model) of the heater, which shall be constructed of corrosion resistant 16-gauge multi-grip floor plate with an OSHA-approved handrail and steel safety chains at each end.  [Indoor suspended models: Structural steel channels shall support the heater and service platform as one. The installing contractor will furnish Hangers and hardware].

C. Vibration Isolators

Vibration isolators shall consist of a steel housing and [an isolation element, 	     	 molded entirely of a colored oil-resistant neoprene for easy identification of 	      capacity / a spring].  The isolators shall have a deflection of 1/4" or less and will be supplied by the manufacturer.  The isolators are to be:

- Shipped loose and field installed (by installer) with a structural steel cradle and threaded rod hangers.

- Shipped loose and field installed (by installer) between the angle clips (welded in place by the manufacturer) and the [site pad / framing].

- Internally installed by the manufacturer for fan and motor isolation from the unit housing. Includes a fabric duct sleeve between the fan discharge and the unit discharge opening.

D. Discharge Plate

Discharge plates shall be provided with heater, as shown on the plans.  These plates will be constructed of 16-gauge corrosion resistant steel, reinforced with angle iron, and painted by the manufacturer.  Contractor shall supply all necessary hanger rods and shall install discharge plate in accordance with manufacturers recommendations.

E. Discharge Head

Manufacturer shall provide a [single deflection (horizontal blades) / double deflection (horizontal and vertical blades)] discharge head(s).  The head will be constructed such that it discharges supply air in [one / three / four] plane(s).  The head shall be constructed of a minimum of 16-gauge aluminized steel.  The directional blades will be 14 gauge aluminized steel and will be adjustable and able to be locked into place.  The discharge head housing will be painted to match the heater.  4-way discharge heads shall be provided with insulation (1"-1-1/2#) installed on the interior floor area for noise reduction.

S:/AASPEC03.doc	12/15/03